## Slide 1: Nuclear Energy Fundamentals Everett Redmond 202-739-8122 elr@nei.org

## Slide 2: Overview
Nuclear Power Plant
Nuclear Process
Major Components & Systems

## Slide 3: Thermal (Steam) Power Plant
Condenser
Cooling Source
Circulating Pump
Heat Source
Coal, Nuclear, Natural Gas, Oil
Turbine Generator
Feed Pump

## Slide 4: Boiling Water Reactor
Condenser
Turbine Generator
Feed Pump
Reactor
Cooling Source
Circulating Pump

## Slide 5: Pressurized Water Reactor
Cooling Source
Circulating Pump
Turbine Generator
Condenser
Main Coolant Pump
Primary Loop
Steam
Generator
Feed Pump
Secondary Loop
Reactor
Cooling Source
Circulating Pump

## Slide 6: Boiling Water – Pressurized Water Reactors
BWR
PWR

## Slide 7: BWR vs. PWR
Reactor Pressure Vessel
Number of Fuel Assemblies
Fuel Rod Array
Number of Control Rods
Type
Operating
Pressure
Inlet Water Temperature
Outlet Steam/Water Temp.
7.1x27.7M 23.3x90.9 ft.
624-800
8x8 – 10x10
145-205
Cruciform
73.1 Kg/cm2
1041.0 psi
215.5 C/420.0 F
287.0 C/550.0 F
4.6x15M
15.0x49.0 ft.
193-241
14x15 - 17x17
77-90
Finger
158 Kg/cm2
2250 psi
280 C/538 F
320 C/610F

## Slide 8: Fuel Assemblies
PWR Fuel
BWR Fuel
~8.4 inches
~5.1 inches
15x15 PWR Fuel Assembly
Relative size of PWR and BWR fuel assemblies
Number of Operating Reactors
PWR – 69, BWR – 35

## Slide 9: YouTube Videos
How does a nuclear reactor work? - NEI
What is a fuel assembly? - NEI
Where do used, or spent, fuel rods go after they are discharged from the reactor? - NEI
Where do used, or spent, fuel assemblies go once the pools inside the reactor building reach capacity? - NEI
What is plutonium and where does it come from? - NEI
Spent Fuel Storage at Diablo Canyon Power Plant – PG&E

## Slide 10: Nuclear Fuel - Uranium
Electrons
Neutrons
Protons
Nucleus
Natural Uranium
  0.7% Uranium-235
  99.3% Uranium-238

## Slide 11: Enrichment
Bank of centrifuges at a URENCO plant

## Slide 12: Nuclear Fission
Energy
Neutron
Fission Products

## Slide 13: Moderator Present – Fission Occurs
Moderator Lost – Fission Does Not Occur

## Slide 14: Plutonium Creation in Reactors

## Slide 15: Difference in Nuclear Fuel
Isotope | Fresh Fuel | Used Fuel
U-238 | 96% | 93%
U-235 | 4% | 1%
Fission Products | 0% | 5%
Plutonium | 0% | 1%
Minor actinides neglected in this table

## Slide 16: PWR Reactor Fuel/Control Rods

## Slide 17: BWR Reactor Fuel/Control Rods

## Slide 18: Reactor Startup
Control Rods
Reactor Shutdown
Reactor Power Increase
Reactor
Core

## Slide 19: Open Fuel Cycle
Ore
Depleted
uranium
Fuel
Enrich
Power
Plant
On-Site or Consolidated
Storage
Electricity
Geologic
Disposal

## Slide 20: Enhanced Fuel Cycle
Fuel
Electricity
Recycling
Geologic
Disposal
Interim
Storage
Fission
Products
Enrich
Ore
Power
Plant
Depleted
uranium

## Slide 21: Safety Principles
Defense-in-Depth
Redundancy & Diversity
Isolation & containment of radioactive material
Training
Conservative decision making at all levels with plant management setting standards
  A culture that strives for excellence

## Slide 22: Defense-in-Depth

## Slide 23: Multiple Barrier Protection
Shield Building Wall
45-inch-thick steel reinforced concrete
Containment Vessel Liner
1/4-inch-thick steel
Dry Well Wall
5-foot-thick reinforced concrete
Bio Shield
4-foot-thick leaded concrete with
1.5-inch-thick steel lining inside and out
Weir Wall
1.5-foot-thick concrete
Reactor Vessel
4- to 8-inches thick steel
Reactor Fuel

## Slide 24: Safety Systems
Pressure – Temperature – Reactivity Control
Pressure
Safety Relief Valves
Primary System
Secondary System
Temperature
Reactor – Coolant Flow - Ultimate Cooling (Heat) Sink
Pumps – Control Valves – Heat Exchangers
Reactivity Control – Control Rods & Boron Injection

## Slide 25: Safety Systems
Shielding
Radiation Protection
Missile Protection
Fire Protection
Physical Separation
Sprinklers & Suppression Systems
Fire Retardation Materials - Fire Doors & Walls
Control Room
Habitability -- Self-Contained
Remote Shut Down Panel
Power Supplies
Emergency Diesel Generator
Batteries

## Slide 26: Power Systems
Feed & Steam Systems
Isolation Valves
Steam Control Valves
Reheaters
Piping
Generation Systems
Turbine-Generator
Hydrogen for cooling
Transformers, switchgear and Offsite Power Supplies

## Slide 27: Support Systems
Fuel Handling
Fuel Handling Equipment
Spent Fuel Pool
New Fuel Storage Area
Spent Fuel Cask Area
Waste Management Area
Decontamination Area
Super Compactor for Dry Waste
Spent Fuel Resin Solidification Area
Water Purification and Clean-Up Systems
Air Conditioning and Filtration Systems

## Slide 28: ESBWR

## Slide 29
Courtesy AREVA
AREVA – EPR – 1600 MWe

## Slide 31: New Design Improvement Examples
AP1000
Safety Valves 1400
Pumps 184
3.6 miles nuclear piping
227 miles, electric cable
Pressurizer 2100 cu. Ft
SG Tube Rupture – No operator action
65% fewer welds
Use of natural phenomena: gravity, natural convection and conduction
1970s 1000MW PWR
Safety Valves 2850
Pumps 280
20.8 miles, nuclear piping
1725 miles, electric cable
Pressurizer – 1400 cu. Ft
SG Tube Rupture – Operator action within 10 mins

## Slide 32: Spent Fuel Pool

## Slide 33: Dry Cask Storage
Vertical Storage Cask
Horizontal Storage Module

## Slide 34
Dual Purpose Canister
On-site Transfer Cask
Transportation Cask
Vertical Storage Cask

## Slide 35: Used Nuclear Fuel Assembly Being Loaded into DPC Basket In Spent Fuel Pool at Nuclear Reactor Site

## Slide 36: DPC Placement into Vertical Storage Cask
Transfer cask is placed atop vertical storage cask
DPC is lowered from transfer cask into vertical storage cask

## Slide 37: Loading Horizontal Storage Modules

## Slide 38: Moving Storage Casks
Crawler
Air Pads
Trailer and JCB Vehicle

## Slide 39: Transportation Cask